Water Solutions Company (WSM)

Technical Specification — Engineering Subcontract

Supply of engineers & per-plant calculations and modifications

In support of: Electrical SPOF Assessment

Central & Eastern sector · 21 assessment units

Document: WSM-SUBC-SPEC-001 · Rev 0 · Classification: Confidential

1 · Purpose & Background

Water Solutions Company (WSM) is executing the urgent assessment of electrical Single Points of Failure (SPOF) 21 assessment units across the Central & Eastern sector groundwater and surface-water desalination plants, over a 4-month contract.

WSM seeks an engineering subcontractor to (a) supply dedicated engineering personnel and (b) provide per-plant calculations and per-plant basic-engineering modifications, as defined below. This specification defines the technical scope, qualifications, deliverables, standards and the pricing structure to be quoted.

2 · Scope of Supply (overview)

| # | Part | Basis | Pricing |
| --- | --- | --- | --- |
| 1 | Supply of personnel — 3 engineers (1 PM — Electrical, 2 Electrical Engineers) | Full-time, 4 months | Lump sum / monthly rate (time-based) |
| 2 | Calculations — electrical power-system studies | Per plant (on call-off) | Unit rate per plant (separately quoted) |
| 3 | Modifications — basic engineering of recommended changes | Per plant (on call-off) | Unit rate per plant (separately quoted) |

Parts 2 and 3 are separate from the personnel supply (Part 1) and are quoted and called off per plant as required by WSM.

3 · Supply of Personnel (full-time, 4 months)

3.1 Headcount & roles

| Role | No. | Engagement |
| --- | --- | --- |
| Project Manager (Electrical Engineer) | 1 | Full-time · 4 months |
| Electrical Engineer | 2 | Full-time · 4 months |
| Total | 3 | Full-time · 4 months |

3.2 Minimum qualifications

| Requirement | Project Manager (Electrical) | Electrical Engineer (×2) |
| --- | --- | --- |
| Degree | BSc Electrical Engineering (MSc/PMP advantageous) | BSc Electrical Engineering |
| Experience | ≥ 10 years | ≥ 5 years |
| LV & MV systems | Required | Required |
| Plant assessment (SPOF / reliability / condition) | Required | Required |
| SCE (Saudi Council of Engineers) accreditation | To Be Discussed | To be Discussed |
| Languages | Arabic & English | Arabic & English |

3.3 Duties & technical scope

The supplied engineers shall work under the direction of WSM's Project Manager and deliver, across the 21 assessment units, the WSM study method (study set SF-01 Document Inventory · SF-02 FMECA · SF-03 Recommendations · SF-04 Site Visit Report):

Review and red-line update of single-line diagrams (SLD); verification against the as-found plant.

Inventory and classification of electrical Single Points of Failure (SPOF); criticality assessment.

FMECA (IEC 60812) and RAM / RBD analysis (IEEE 493 / ISO 20815); ISO 14224 taxonomy.

Field surveys (non-intrusive) at the host plants; data capture; QHSE-compliant site work.

Support to the per-plant calculations (Part 2) and modifications (Part 3) and to the final report.

Perform Basic Calculations:
-Load-flow analysis;

- -Short-circuit study;

- -Protection coordination study;

- -Arc-flash / incident-energy study (IEEE 1584);

- -Earthing & lightning-protection assessment.

Standards: IEC, IEEE (incl. IEEE 1584 / IEEE 493), NFPA 70E, ANSI, NEMA.

3.4 Location, hours & reporting

Work is performed at WSM's premises and plant sites (Central & Eastern — Riyadh, Madinah, Qassim, Eastern Region) as required. Personnel are full-time and dedicated to this project for the 4-month term and report to the WSM Project Manager.

Pricing: a unit rate per plant, quoted in the pricing schedule (§9, Item 2).

4 · Modifications: Basic Engineering (per plant, separately quoted)

On call-off per plant, the subcontractor shall provide the basic (concept) engineering of the modifications recommended by the assessment, comprising (as applicable):

Revised / marked-up single-line diagram for the proposed modification;

Equipment sizing and outline technical specifications (e.g., bus-tie auto-transfer scheme, standby/alternate feeds, protection re-grading, battery/charger, earthing remediation);

Perform Basic Calculations on the modifications:
-Load-flow analysis;

- -Short-circuit study;

- -Protection coordination study;

- -Arc-flash / incident-energy study (IEEE 1584);

- -Earthing & lightning-protection assessment.

Scheme description, interface/sequence of operation, plot plan, an indicative bill of materials (high level).

Battery limit: basic engineering only — concept level. Excludes detailed design, procurement and construction.

Deliverable per plant: a basic-engineering package per modification (or per plant set of modifications).

Pricing: a unit rate per plant, quoted in the pricing schedule (§9, Item 3).

5 · Duration & Programme

Part 1 (personnel): 4 months, full-time, from the mobilization date notified by WSM.

Parts 2 & 3 (calculations / modifications): per call-off; turnaround per plant to be stated by the subcontractor in its offer.

6 · HSE, Quality, Confidentiality & Compliance

QHSE: comply with WSM's integrated management system (ISO 9001/14001/45001) [to be agreed] and host-plant permit-to-work and HSE rules; non-intrusive survey only.

Quality: deliverables subject to WSM review and where required to review/stamp by an SCE-accredited engineer (quoted separately).

Confidentiality & data: sign WSM's NDA; handle client data under the NCA cybersecurity requirements (v6.0); no retention or disclosure of SWA data.

Intellectual property: all deliverables and models vest in WSM / the client.

Statutory: valid CR, SCE accreditation for staff, Saudization, GOSI and tax compliance.

7 · Submittals required with the offer

CVs of the proposed 3 engineers evidencing the §3.2 qualifications (with SCE numbers if applicable).

Company profile, relevant experience and references.

Method statement for Parts 2 & 3, and the software tools to be used.

The completed pricing schedule (§9).

8 · Pricing Schedule (to be completed by the subcontractor)

| # | Item | Unit / basis | Qty | Rate (SAR) | Amount (SAR) |
| --- | --- | --- | --- | --- | --- |
| 1 | Supply of 3 engineers (1 PM-Electrical + 2 Electrical), full-time | per month (×3 staff) | 4 months | [ … ] | [ … ] |
| 2 | Calculations (load-flow, short-circuit, protection coordination, arc-flash, earthing & lightning) | per plant | per call-off | [ … ] | [ … ] |
| 3 | Modifications — basic engineering of recommended changes | per plant | per call-off | [ … ] | [ … ] |

Quote each item separately. Item 1 is a fixed 4-month full-time engagement for the three engineers; Items 2 and 3 are unit rates per plant, called off by WSM as required. All rates exclusive of VAT; VAT to be shown separately. Prices are firm for the engagement period.